{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":48,"n_cols":10,"rows_kept":48,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWWQ-KC"]
[]
[]
[]
[]
["","","","","","EWWQ014KCW1N","EWWQ025KCW1N","EWWQ033KCW1N","EWWQ049KCW1N","EWWQ064KCW1N"]
["Hangnyomás szint","Hűtés","","Névl.","dB(A)","55.2","55.2","62.1","57.6","64.6"]
["Refrigerant","Áramkörök","","Mennyiség","","1","1","1","2","2"]
["","GWP","","","","2,088.0","2,088.0","2,088.0","2,088.0","2,088.0"]
["","Feltöltés","","","kg","0.0, 1.30","0.0, 1.90","0.0, 2.70","0.0, 4.60","0.0, 6.80"]
["","Típus","","","","R-410A","R-410A","R-410A","R-410A","R-410A"]
["Működési tartomány","Párologtató","Hűtés","Min.","°C száraz hőm.","-10","-10","-10","-10","-10"]
["","","","Max.","°C száraz hőm.","20","20","20","20","20"]
["Hűtési teljesítmény","Névl.","","","kW","12.09, 13.25","19.87, 23.89","28.90, 30.47","39.35, 47.15","57.84, 61.00"]
["Elektromos bemenet","Hűtés","","Névl.","kW","3.20, 3.74","5.70, 6.11","7.30, 8.43","11.4, 12.03","14.6, 16.41"]
["","Fűtés","","Névl.","kW","3.90","7.10","8.70","14.4","17.5"]
["Sound power level","Hűtés","","Névl.","dB(A)","69","69","76","72","79"]
["COP","","","","","3.84","3.83","3.98","3.77","3.98"]
["Kompresszor","Típus","","","","Kúpos kompresszor","Kúpos kompresszor","Kúpos kompresszor"]
["","Mennyiség_","","","","1","1","1"]
["Méretek","Egység","","Szélesség","mm","600","600","600","600","600"]
["","","","Mélység","mm","600","600","600","1,200","1,200"]
["","","","Magasság","mm","600","600","600","600","600"]
["Kapacitás-szabályozás","Minimális kapacitás","","","%","100","100","100","50","50"]
["","Eljárás","","","","Rögzített","Rögzített","Rögzített","Rögzített","Rögzített"]
["Felületfűtés","55°C kilépő víz hőmérséklet, átlagos klíma","Általános","Seasonal space heating eff. class","","A++","A++","A++","A++","A++"]
["","","","ηs (Szezonális felületfűtési hatékonyság)","%","138","137","140"]
["","","","SCOP","","3.64","3.63","3.71","3.58","3.87"]
["Tömeg","Üzemi súly","","","kg","70, 74","129, 136","135, 145","247, 266","258, 282"]
["","Egység","","","kg","68.0","132","141","257","265"]
["A vizes hőcserélő ürítése  - párologtató","Típus","","","","Forrasztott lemez","Forrasztott lemez","Forrasztott lemez","Forrasztott lemez","Forrasztott lemez"]
["","Vízmennyiség","","","l","1.47","1.96","2.74","4.47","5.88"]
["EER","","","","","3.237, 4.20","3.254, 4.18","3.429, 4.16","3.27, 4.13","3.524, 4.18"]
["Fűtőkapacitás","Névl.","","","kW","14.98","27.30","34.74","54.13","69.51"]
["Power supply","fázis","","","","3N~","3N~","3N~","3N~","3N~"]
["","Frekvencia","","","Hz","50","50","50","50","50"]
["","Feszültség","","","V","400","400","400","400","400"]
["Notes","","","","","(1) - Hűtés: EW 12℃; LW 7℃; környezeti körülmények: 35°C száraz hőm.","(1) - Hűtés: EW 12℃; LW 7℃; környezeti körülmények: 35°C száraz hőm.","(1) - Hűtés: EW 12℃; LW 7℃; környezeti körülmények: 35°C száraz hőm.","(1) - Hűtés: EW 12℃; LW 7℃; környezeti körülmények: 35°C száraz hőm.","(1) - Hűtés: EW 12℃; LW 7℃; környezeti körülmények: 35°C száraz hőm."]
["","","","","","(2) - Hűtés: EW 23℃; LW 18℃; környezeti körülmények: 35°C száraz hőm.","(2) - Hűtés: EW 23℃; LW 18℃; környezeti körülmények: 35°C száraz hőm.","(2) - Hűtés: EW 23℃; LW 18℃; környezeti körülmények: 35°C száraz hőm.","(2) - Hűtés: EW 23℃; LW 18℃; környezeti körülmények: 35°C száraz hőm.","(2) - Hűtés: EW 23℃; LW 18℃; környezeti körülmények: 35°C száraz hőm."]
["","","","","","(3) - Feltétel: Tkörny DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Feltétel: Tkörny DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Feltétel: Tkörny DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Feltétel: Tkörny DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Feltétel: Tkörny DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)"]
["","","","","","(4) - Feltétel: Tkörny DB/WB 7°C/6°C - LWC 45℃ (Dt=5°C)","(4) - Feltétel: Tkörny DB/WB 7°C/6°C - LWC 45℃ (Dt=5°C)","(4) - Feltétel: Tkörny DB/WB 7°C/6°C - LWC 45℃ (Dt=5°C)","(4) - Feltétel: Tkörny DB/WB 7°C/6°C - LWC 45℃ (Dt=5°C)","(4) - Feltétel: Tkörny DB/WB 7°C/6°C - LWC 45℃ (Dt=5°C)"]
["","","","","","(5) - Az EN14825 szabvány szerint","(5) - Az EN14825 szabvány szerint","(5) - Az EN14825 szabvány szerint","(5) - Az EN14825 szabvány szerint","(5) - Az EN14825 szabvány szerint"]
["","","","","","(6) - A üzemelési módtól függ, lásd az összeszerelési kézikönyvet.","(6) - A üzemelési módtól függ, lásd az összeszerelési kézikönyvet.","(6) - A üzemelési módtól függ, lásd az összeszerelési kézikönyvet.","(6) - A üzemelési módtól függ, lásd az összeszerelési kézikönyvet.","(6) - A üzemelési módtól függ, lásd az összeszerelési kézikönyvet."]
["","","","","","(7) - További részleteket lásd az üzemi tartomány ábrán","(7) - További részleteket lásd az üzemi tartomány ábrán","(7) - További részleteket lásd az üzemi tartomány ábrán","(7) - További részleteket lásd az üzemi tartomány ábrán","(7) - További részleteket lásd az üzemi tartomány ábrán"]
["Kompresszor","Típus","","","","","","","Kúpos kompresszor","Kúpos kompresszor"]
["","Mennyiség_","","","","","","","2","2"]
["Felületfűtés","35°C kilépő víz hőm., átlagos klíma","Általános","SCOP","","","","","4.87","4.91"]
["","","","Szezonális felületfűtési hatékonysági osztály","","","","","A+++","A+++"]