{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":60,"n_cols":9,"rows_kept":60,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWYA-DW1P-H-"]
[]
[]
[]
[]
["","","","","","EWYA009DAW1P-H-","EWYA011DAW1P-H-","EWYA014DAW1P-H-","EWYA016DAW1P-H-"]
["Hangnyomás szint","Hűtés","","Névl.","dB(A)","44.0","47.7","50.8","51.0"]
["Hidraulikus alkatrészek","Tágulási tartály","","Mennyiség","l","8","8","8","8"]
["Üzemi tartomány","Levegőoldal","Hűtés","Min.","°C száraz hőm.","10","10","10","10"]
["","","","Max.","°C száraz hőm.","43","43","43","43"]
["","","Fűtés","Max.","°C száraz hőm.","25","25","25","25"]
["","","","Min.","°C száraz hőm.","-25","-25","-25","-25"]
["","Vízoldal","Fűtés","Min.","°C száraz hőm.","9 (7)","9 (7)","9 (7)","9 (7)"]
["","","","Max.","°C száraz hőm.","60 (7)","60 (7)","60 (7)","60 (7)"]
["","","Hűtés","Max.","°C száraz hőm.","22","22","22","22"]
["","","","Min.","°C száraz hőm.","5","5","5","5"]
["Hűtőközeg töltet","Áramkörönként","","","kg","3.80","3.80","3.80","3.80"]
["","Refrigerant charge-=-Per circuit-=-TCO2Eq","","","TCO2Eq","2.6","2.6","2.6","2.6"]
["Kompresszor","Type","","","","Hermetikusan zárt lengő, inverteres kompresszor","Hermetikusan zárt lengő, inverteres kompresszor","Hermetikusan zárt lengő, inverteres kompresszor","Hermetikusan zárt lengő, inverteres kompresszor"]
["","Starting method","","","","Inverterrel hajtott","Inverterrel hajtott","Inverterrel hajtott","Inverterrel hajtott"]
["","Mennyiség_","","","","1","1","1","1"]
["Levegő hőcserélő","Típus","","","","Nagy hatékonyságú borda- és csőtípus egy darabból készült túlhűtővel","Nagy hatékonyságú borda- és csőtípus egy darabból készült túlhűtővel","Nagy hatékonyságú borda- és csőtípus egy darabból készült túlhűtővel","Nagy hatékonyságú borda- és csőtípus egy darabból készült túlhűtővel"]
["Tömeg","Egység","","","kg","147","147","147","147"]
["EER","","","","","3.35 (1), 5.34 (2)","3.26 (1), 5.31 (2)","3.16 (1), 5.04 (2)","3.06 (1), 4.74 (2)"]
["Refrigerant","GWP","","","","675.0","675.0","675.0","675.0"]
["","Típus","","","","R-32","R-32","R-32","R-32"]
["","Áramkörök","","Mennyiség","","1","1","1","1"]
["","Vezérlés","","","","Elektronikus expanziós szelep","Elektronikus expanziós szelep","Elektronikus expanziós szelep","Elektronikus expanziós szelep"]
["Ventilátormotor","Sebesség","Hűtés","Névl.","1/perc","500","550","650","650"]
["","","Fűtés","Névl.","1/perc","400","450","550","650"]
["Hűtési teljesítmény","Névl.","","","kW","9.35 (1), 9.10 (2)","11.6 (1), 11.5 (2)","12.8 (1), 12.7 (2)","14.0 (1), 15.3 (2)"]
["Vizes hőcserélő","Vízmennyiség","","","l","2","2","2","2"]
["","Minimális vízmennyiség a rendszerben","","","l","50 (6)","50 (6)","50 (6)","50 (6)"]
["","Típus","","","","Lemezes hőcserélő","Lemezes hőcserélő","Lemezes hőcserélő","Lemezes hőcserélő"]
["Áramfelvétel","Hűtés","","Névl.","kW","2.79 (1), 1.71 (2)","3.56 (1), 2.17 (2)","4.06 (1), 2.51 (2)","4.58 (1), 3.24 (2)"]
["","Fűtés","","Névl.","kW","1.91 (3), 2.43 (4)","2.18 (3), 2.68 (4)","2.46 (3), 3.42 (4)","3.53 (3), 4.56 (4)"]
["Hangteljesítmény szintje","Hűtés","","Névl.","dB(A)","65.5","67.0","69.0","69.0"]
["COP","","","","","4.91 (3), 3.71 (4)","4.83 (3), 3.66 (4)","4.87 (3), 3.64 (4)","4.53 (3), 3.51 (4)"]
["Méretek","Berendezés","","Szélesség","mm","1,380","1,380","1,380","1,380"]
["","","","Mélység","mm","460","460","460","460"]
["","","","Magasság","mm","870","870","870","870"]
["Teljesítmény szabályozás","Eljárás","","","","Változó (inverter)","Változó (inverter)","Változó (inverter)","Változó (inverter)"]
["Felületfűtés","55°C kilépő víz hőmérséklet, átlagos klíma","Általános","Seasonal space heating eff. class","","A++","A++","A++","A++"]
["","","","ηs (Szezonális felületfűtési hatékonyság)","%","135","132","134","132"]
["","","","SCOP","","3.44","3.37","3.42","3.37"]
["Ventilátor","Légáramlási arány","Fűtés","Névl.","m³/perc","48.0","55.8","70.4","85.0"]
["","","Hűtés","Névl.","m³/perc","63","70","85","85"]
["Fűtőkapacitás","Névl.","","","kW","9.37 (3), 9.00 (4)","10.6 (3), 9.82 (4)","12.0 (3), 12.5 (4)","16.0 (3), 16.0 (4)"]
["Kompresszor","Starting method","","","","Inverter","Inverter","Inverter","Inverter"]
["Power supply","fázis","","","","3~","3~","3~","3~"]
["","Frekvencia","","","Hz","50","50","50","50"]
["","Megnevezés","","","","W1","W1","W1","W1"]
["","Feszültség","","","V","400","400","400","400"]
["Notes","","","","","(1) - Hűtés: EW 12℃; LW 7℃; környezeti körülmények: 35°C száraz hőm.","(1) - Hűtés: EW 12℃; LW 7℃; környezeti körülmények: 35°C száraz hőm.","(1) - Hűtés: EW 12℃; LW 7℃; környezeti körülmények: 35°C száraz hőm.","(1) - Hűtés: EW 12℃; LW 7℃; környezeti körülmények: 35°C száraz hőm."]
["","","","","","(2) - Hűtés: EW 23℃; LW 18℃; környezeti körülmények: 35°C száraz hőm.","(2) - Hűtés: EW 23℃; LW 18℃; környezeti körülmények: 35°C száraz hőm.","(2) - Hűtés: EW 23℃; LW 18℃; környezeti körülmények: 35°C száraz hőm.","(2) - Hűtés: EW 23℃; LW 18℃; környezeti körülmények: 35°C száraz hőm."]
["","","","","","(3) - Feltétel: Tkörny DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Feltétel: Tkörny DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Feltétel: Tkörny DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Feltétel: Tkörny DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)"]
["","","","","","(4) - Feltétel: Tkörny DB/WB 7°C/6°C - LWC 45℃ (Dt=5°C)","(4) - Feltétel: Tkörny DB/WB 7°C/6°C - LWC 45℃ (Dt=5°C)","(4) - Feltétel: Tkörny DB/WB 7°C/6°C - LWC 45℃ (Dt=5°C)","(4) - Feltétel: Tkörny DB/WB 7°C/6°C - LWC 45℃ (Dt=5°C)"]
["","","","","","(5) - Az EN14825 szabvány szerint","(5) - Az EN14825 szabvány szerint","(5) - Az EN14825 szabvány szerint","(5) - Az EN14825 szabvány szerint"]
["","","","","","(6) - A üzemelési módtól függ, lásd az összeszerelési kézikönyvet.","(6) - A üzemelési módtól függ, lásd az összeszerelési kézikönyvet.","(6) - A üzemelési módtól függ, lásd az összeszerelési kézikönyvet.","(6) - A üzemelési módtól függ, lásd az összeszerelési kézikönyvet."]
["","","","","","(7) - További részleteket lásd az üzemi tartomány ábrán","(7) - További részleteket lásd az üzemi tartomány ábrán","(7) - További részleteket lásd az üzemi tartomány ábrán","(7) - További részleteket lásd az üzemi tartomány ábrán"]