{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":77,"n_cols":11,"rows_kept":77,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWXT-ATV3"]
[]
[]
[]
[]
["","","","","","FWXT10ABTV3","FWXT15ABTV3","FWXT20ABTV3","FWXT10AATV3 (Archived)","FWXT15AATV3 (Archived)","FWXT20AATV3 (Archived)"]
["Méretek","Egység","","Szélesség","mm","","","","902","1,100","1,300"]
["","","","Mélység","mm","","","","128","128","128"]
["","","","Magasság","mm","","","","335","335","335"]
["Burkolat","Szín","","","","","","","RAL 9003","RAL 9003","RAL 9003"]
["Tömeg","Egység","","","kg","","","","14.0","16.0","19.0"]
["Power supply","fázis","","","","","","","1~","1~","1~"]
["","Frekvencia","","","Hz","","","","50","50","50"]
["","Feszültség","","","V","","","","230","230","230"]
["Hűtési teljesítmény","7/12°C","","Min.","kW","0.49","0.62","0.70"]
["","","","Köz.","kW","0.88","1.08","1.21"]
["","","","Max.","kW","1.24","1.61","1.94"]
["Érezhető hűtési teljesítmény","7/12°C","","Min.","kW","0.37","0.52","0.57"]
["","","","Köz.","kW","0.70","0.86","1.02"]
["","","","Max.","kW","0.98","1.27","1.52"]
["Fűtési teljesítmény","45/40°C","","Min.","kW","0.55","0.79","0.74"]
["","","","Köz.","kW","1.00","1.36","1.55"]
["","","","Max.","kW","1.50","2.01","2.13"]
["Áramfelvétel","Min.","","","kW","0.01","0.01","0.01"]
["","Köz.","","","kW","0.01","0.01","0.01"]
["","Max.","","","kW","0.02","0.02","0.03"]
["Ventilátor sebesség","Min.","","","1/perc","680.00","680.00","680.00"]
["","Köz.","","","1/perc","1100.00","1100.00","1100.00"]
["","Max.","","","1/perc","1500.00","1500.00","1500.00"]
["Burkolat","Szín","","","","RAL 9003","RAL 9003","RAL 9003"]
["","Anyag","","","","Fémlemez","Fémlemez","Fémlemez"]
["Méretek","Egység","","Magasság","mm","335","335","335"]
["","","","Szélesség","mm","902","1102","1302"]
["","","","Mélység","mm","128","128","128"]
["","Becsomagolt egység","","Magasság","mm","490","490","490"]
["","","","Szélesség","mm","1030","1230","1430"]
["","","","Mélység","mm","210","210","210"]
["Tömeg","Egység","","","kg","14","16","19"]
["","Becsomagolt egység","","","kg","15","17","20"]
["Csomagolás","Anyag","","","","Karton","Karton","Karton"]
["","Súly","","","kg","1","1","1"]
["Hőcserélő","Mennyiség","","","","1","1","1"]
["","Belső tekercs mennyisége","","","l","0.5","0.61","0.77"]
["","Töltés","","Üzemi nyomás","bar","10","10","10"]
["Víz kör","Csőcsatlakozások átmérője","","","hüvelyk","3/4","3/4","3/4"]
["Vízkör","Csővezeték anyaga","","","","RÉZ","RÉZ","RÉZ"]
["","Nyomás","Fűtés","Max.","bar","10","10","10"]
["Vízrendszer – Víznyomás-esés","Fűtés","45/40°C","Min.","kPa","5.10","4.81","6.00"]
["","","","Köz.","kPa","12.00","6.30","6.40"]
["","","","Max.","kPa","16.30","7.20","8.10"]
["","Hűtés","7/12°C","Min.","kPa","4.80","4.70","5.50"]
["","","","Köz.","kPa","10.50","5.60","5.40"]
["","","","Max.","kPa","11.70","5.10","5.30"]
["Vízrendszer – víz áramlási sebessége","Fűtés","45/40°C","Min.","kg/h","100.00","140","150.00"]
["","","","Köz.","kg/h","170.00","240","300.00"]
["","","","Max.","kg/h","260.00","350","420.00"]
["","Hűtés","7/12°C","Min.","kg/h","80.00","110","120.00"]
["","","","Köz.","kg/h","150.00","190","210.00"]
["","","","Max.","kg/h","210.00","280","330.00"]
["Hangteljesítményszint","Min.","","","dB(A)","35","36","37"]
["","Köz.","","","dB(A)","46","47","48"]
["","Max.","","","dB(A)","53.0","54.0","55.0"]
["Üzemi tartomány","Fűtés","Vízoldal","Min.","°C","30","30","30"]
["","","","Max.","°C","85","85","85"]
["","Hűtés","Vízoldal","Min.","°C","5","5","5"]
["","","","Max.","°C","18","18","18"]
["","Beltéri telepítés","Környezeti","Min.","°C száraz hőm.","0","0","0"]
["","","","Max.","°C száraz hőm.","45","45","45"]
["Vezérlőrendszerek","Infravörös távszabályzó","","","","Az FWXT-ATV3(C)(CL) típushoz","Az FWXT-ATV3(C)(CL) típushoz","Az FWXT-ATV3(C)(CL) típushoz"]
["","A beltéri egységbe beszerelve","","","","Igen","Igen","Igen"]
["Áramellátás","fázis","","","","1~","1~","1~"]
["","Frekvencia","","","Hz","50","50","50"]
["","Feszültség","","","V","230","230","230"]
["Áramfogyasztás","Max.","","","W","19","20","29"]
["","Készenlét","","","W","3","4","5"]
["Áram","Maximális működési áram","","Fűtés","A","0.16","0.18","0.24"]
["","Maximális üzemi áram","","Hűtés","A","0.16","0.18","0.24"]