{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":74,"n_cols":9,"rows_kept":74,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RZAG-MV1"]
[]
[]
[]
[]
["","","","","","RZAG71M7V1B","RZAG100M7V1B","RZAG125M7V1B","RZAG140M7V1B"]
["Hangnyomás szint","Fűtés","","Névl.","dB(A)","","","","52"]
["","Hűtés","","Névl.","dB(A)","","","","51"]
["Standard Accessories","Szalagkötések","","","","","","","2"]
["","Telepítési utasítás","","","","","","","1"]
["","Hűtőközeg címkéje az F-gáz szabályozáshoz","","","","","","","1"]
["","Általános biztonsági óvintézkedések","","","","","","","1"]
["","LOT10 Energetikai címke","","","","","","","1"]
["Refrigerant","Charge","","","TCO2Eq","","","","2.53"]
["","GWP","","","","","","","675"]
["","Töltet","","","kg","","","","3.75"]
["","Típus","","","","","","","R-32"]
["Csőcsatlakozások","Folyadék","","Külső átm.","pp","","","","9.52"]
["","Csőhossz","Max.","OU - IU","m","","","","85"]
["","","Rendszer","Terhelés nélkül","m","","","","40"]
["","","","Egyenlő","m","","","","100"]
["","Gáz","","Külső átm.","pp","","","","15.9"]
["","Szintkülönbség","IU - IU","Max.","m","","","","0.5"]
["","","IU - OU","Max.","m","","","","30.0"]
["","További hűtőközeg utántöltés","","","kg/m","","","","Lásd az összeszerelési kézikönyvet"]
["Sound power level","Hűtés","","","dB(A)","","","","70"]
["","Fűtés","","","dB(A)","","","","70 (1)"]
["Kompresszor","Type","","","","","","","Hermetikusan zárt lengő kompresszor"]
["Méretek","Egység","","Szélesség","pp","","","","940"]
["","","","Mélység","pp","","","","320"]
["","","","Magasság","pp","","","","1,430"]
["Tömeg","Egység","","","kg","","","","92"]
["Power supply","fázis","","","","","","","1~"]
["","Frekvencia","","","Hz","","","","50"]
["","Feszültség","","","V","","","","220-240"]
["Notes","","","","","","","","(1) - Az ENER Lot 21 szerint"]
["","","","","","","","","(2) - A fázisonként nagyobb mint 16 A és ≤ 75 A közötti bemeneti áramú kisfeszültségű rendszerhez csatlakozó készülékek által létrehozott harmonikus áram határértékeit meghatározó európai/nemzetközi műszaki szabvány."]
["","","","","","","","","(3) - Ssc: rövidzárlati áram"]
["","","","","","","","","(4) - A fázisonként ≤ 16A bemeneti áramú kisfeszültségű rendszerhez csatlakozó készülékek által létrehozott harmonikus áram határértékeit meghatározó európai/nemzetközi műszaki szabvány."]
["Méretek","Egység","","Magasság","pp","990","1430","1430"]
["","","","Szélesség","pp","940","940","940"]
["","","","Mélység","pp","320","320","320"]
["Tömeg","Egység","","","kg","70","92","92"]
["Kompresszor","Típus","","","","Hermetikusan zárt lengő kompresszor","Hermetikusan zárt lengő kompresszor","Hermetikusan zárt lengő kompresszor"]
["Üzemi tartomány","Hűtés","Környezeti","Min.","°C száraz hőm.","-20","-20","-20"]
["","","","Max.","°C száraz hőm.","52","52","52"]
["","Fűtés","Környezeti","Min.","°C párás hőm.","-20","-20","-20"]
["","","","Max.","°C párás hőm.","18.0","18.0","18.0"]
["Hangteljesítményszint","Hűtés","","","dB(A)","64","66","69"]
["Hangnyomás szint","Hűtés","","Névl.","dB(A)","46","47","50"]
["","Fűtés","","Névl.","dB(A)","49","51","52"]
["Hűtőközeg","Típus","","","","R-32","R-32","R-32"]
["","Töltet","","","kg","2.95","3.75","3.75"]
["","GWP","","","","675","675","675"]
["","Töltet","","","tCO2Eq","1.99","2.53","2.53"]
["Csőcsatlakozások","Folyadék","","Külső átm.","pp","9.52","9.52","9.52"]
["","Gáz","","Külső átm.","pp","15.9","15.9","15.9"]
["","Csőhossz","Max.","OU - IU","m","55","85","85"]
["","","Rendszer","Egyenlő","m","75","100","100"]
["","","","Terhelés nélkül","m","40","40","40"]
["","További hűtőközeg utántöltés","","","kg/m","Lásd az összeszerelési kézikönyvet","Lásd az összeszerelési kézikönyvet","Lásd az összeszerelési kézikönyvet"]
["","Szintkülönbség","IU - OU","Max.","m","30.0","30.0","30.0"]
["","","IU - IU","Max.","m","0.5","0.5","0.5"]
["Standard Accessories","Installation manual","","","","1","1","1"]
["","Refrigerant label for F-gas regulation","","","","1","1","1"]
["","General safety precautions","","","","1","1","1"]
["","LOT10 Energy Label","","","","1","1","1"]
["","Tie-wraps","","","","2","2","2"]
["Áramellátás","fázis","","","","1~","1~","1~"]
["","Frekvencia","","","Hz","50","50","50"]
["","Feszültség","","","V","220-240","220-240","220-240"]
["Áramerősség - 50Hz","A biztosítékok maximálisan felvett áramerőssége (MFA)","","","A","20","32","32"]
["Hangteljesítményszint","Fűtés","","","dB(A)","","","69 (1)"]
["Notes","","","","","","","(1) - Az ENER Lot 21 szerint"]