{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":41,"n_cols":13,"rows_kept":41,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RZAG-NY1"]
[]
[]
[]
[]
["","","","","","RZAG71N2Y1B","RZAG71N7Y1B","RZAG100N7Y1B","RZAG100N2Y1B","RZAG125N7Y1B","RZAG125N2Y1B","RZAG140N7Y1B","RZAG140N2Y1B"]
["Méretek","Egység","","Magasság","pp","870","870","870","870","870","870","870","870"]
["","","","Szélesség","pp","1100","1100","1100","1100","1100","1100","1100","1100"]
["","","","Mélység","pp","460","460","460","460","460","460","460","460"]
["Tömeg","Egység","","","kg","81","81","85","85","94","94","94","94"]
["Kompresszor","Típus","","","","Hermetikusan zárt lengő kompresszor","Hermetikusan zárt lengő kompresszor","Hermetikusan zárt lengő kompresszor","Hermetikusan zárt lengő kompresszor","Hermetikusan zárt lengő kompresszor","Hermetikusan zárt lengő kompresszor","Hermetikusan zárt lengő kompresszor","Hermetikusan zárt lengő kompresszor"]
["Üzemi tartomány","Hűtés","Környezeti","Min.","°C száraz hőm.","-20","-20","-20","-20","-20","-20","-20","-20"]
["","","","Max.","°C száraz hőm.","52","52","52","52","52","52","52","52"]
["","Fűtés","Környezeti","Min.","°C párás hőm.","-20","-20","-20","-20","-20","-20","-20","-20"]
["","","","Max.","°C párás hőm.","18","18","18","18","18","18","18","18"]
["Hangteljesítményszint","Hűtés","","","dB(A)","64","64","66","66","69","69","70","70"]
["","Fűtés","","","dB(A)","","","","","68 (1)","68 (1)","71 (1)","71 (1)"]
["Hangnyomás szint","Hűtés","","Névl.","dB(A)","46","46","47","47","49","49","50","50"]
["","Fűtés","","Névl.","dB(A)","48","48","50","50","52","52","52","52"]
["Hűtőközeg","Típus","","","","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32"]
["","Töltet","","","kg","3.20","3.2","3.2","3.20","3.7","3.70","3.7","3.70"]
["","GWP","","","","675","675","675","675","675","675","675","675"]
["","Töltet","","","tCO2Eq","2.16","2.16","2.16","2.16","2.5","2.50","2.5","2.50"]
["Csőcsatlakozások","Folyadék","","Külső átm.","pp","10","10","10","10","10","10","10","10"]
["","Gáz","","Külső átm.","pp","15.9","15.9","15.9","15.9","15.9","15.9","15.9","15.9"]
["","Csőhossz","Max.","OU - IU","m","55","55","85","85","85","85","85","85"]
["","","Rendszer","Egyenlő","m","75","75","100","100","100","100","100","100"]
["","","","Terhelés nélkül","m","40","40","40","40","40","40","40","40"]
["","További hűtőközeg utántöltés","","","kg/m","Lásd az összeszerelési kézikönyvet","Lásd az összeszerelési kézikönyvet","Lásd az összeszerelési kézikönyvet","Lásd az összeszerelési kézikönyvet","Lásd az összeszerelési kézikönyvet","Lásd az összeszerelési kézikönyvet","Lásd az összeszerelési kézikönyvet","Lásd az összeszerelési kézikönyvet"]
["","Szintkülönbség","IU - OU","Max.","m","30","30","30","30","30","30","30","30"]
["","","IU - IU","Max.","m","0.5","0.5","0.5","0.5","0.5","0.5","0.5","0.5"]
["Standard Accessories","Installation manual","","","","1","1","1","1","1","1","1","1"]
["","Refrigerant label for F-gas regulation","","","","1","1","1","1","1","1","1","1"]
["","General safety precautions","","","","1","1","1","1","1","1","1","1"]
["","Peel off F-gas label","","","","1","1","1","1","1","1","1","1"]
["","Tie-wraps","","","","2","2","2","2","2","2","2","2"]
["Áramellátás","fázis","","","","3~","3~","3~","3~","3~","3~","3~","3~"]
["","Frekvencia","","","Hz","50","50","50","50","50","50","50","50"]
["","Feszültség","","","V","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415"]
["Áramerősség - 50Hz","A biztosítékok maximálisan felvett áramerőssége (MFA)","","","A","16","16","16","16","16","16","16","16"]
["Notes","","","","","","","","","(1) - Az ENER Lot 21 szerint","(1) - Az ENER Lot 21 szerint","(1) - Az ENER Lot 21 szerint","(1) - Az ENER Lot 21 szerint"]